## Slide 1: TRAINING PROGRAMME FOR INDUSTRIAL ENTERPRISEs
Module 8.6:
Energy efficiency opportunities in the textile production lines.
TECHNICAL STAFFS

## Slide 2: CONTENT
Energy efficiency opportunities in yarn production
Energy efficiency opportunities in wet processing
Energy efficiency opportunities in garment production

## Slide 3: I. Energy efficiency opportunities in yarn production

## Slide 4
Energy Performance Improvement Options
Compressed air system
  Demand side Pressure optimization
  Leakage reduction
Ventilation and Humidification Plant
  3-5% positive pressure between supply and exhaust air
  Automated controls of humidification system
    Optimization of Supply and Return Fans e.g. FRP Fans, Air Changes..
    Optimization of Showering System e.g. Fogging System, Humidity feedback control…
Machinery
  Automation & synchronization of transportation fans in blow room
  Avoiding fluff accommodation in machines to reduce friction and yarn breakages (especially Ring frames and Auto Cone)
  Automation of machine speed according to yarn tension and loading in Ring frames
I. Energy efficiency opportunities in yarn production

## Slide 5: USE OF EFFICIENT MATERIALS AND PROCESSES
Polymers fiber products with optimized properties, including improved dye ability.
Soaping, washing / rinsing process after dyeing reduced the processing time and water consumption compared to the conventional system.
I. Energy efficiency opportunities in yarn production

## Slide 6: USE OF EFFICIENT PROCESSES
Color Fast Finish (BASF), is a one-step-process of textile can reduce the processing time and carbon dioxide emissions.
BASF COLOR FAST FINISH
Innovative machine that applies finishes to fabrics using foam, which conserves water.
Gaston Foam applicator technology can also be used for foam dyeing and finishing processes.
I. Energy efficiency opportunities in yarn production

## Slide 7: USE OF EFFICIENT PROCESSES
The revolutionary air technology for dyeing requires only one-forth of water and also reduces energy and chemicals consumption.
Digital printing, using ink from the dyes, wastes neither fabric nor ink and does not use harmful salts and significantly reduces the environmental footprint.
Formaldehyde-free pigment printing system, which ensures "zero add-on" of formaldehyde during production and needs no further treatment.
Industrial enzymes to replace harsh chemicals, which reduces energy costs, water consumption and also improves the feel of the fabric.
I. Energy efficiency opportunities in yarn production

## Slide 8: PROCESS COOLING WATER RECYCLING
Discharged cooling water from applications such as singeing and pre-shrinking is often both clean and of sufficiently high temperature for it to be recovered and reused directly for dyeing and finishing process, such as de-sizing, scouring, washing, or rinsing.
This can help reduce thermal energy demand and water consumption, with related energy savings from lower pumping demand.
Practice | Water Saving | Energy Saving (Steam) | Typical Pay Back Period
Reuse of Cooling Water | 1 - 5% | 1 - 3% | < 1.2 Years
I. Energy efficiency opportunities in yarn production

## Slide 9: RINSE WATER HEAT RECOVERY
In a textile mill fabric is rinsed with large quantities of very hot (typically 80 °C) water.
Waste heat from used rinse water can be recovered for preheating incoming water for the next hot rinse.
This also helps to reducing the temperature of the wastewater prior to treatment which can reduce or eliminate the need for energy use in treatment plant cooling towers
Practice | Energy Saving | Typical Pay Back Period
Recover Heat from Hot Rinse Water | 2 - 12% | 2 - 4 Months
I. Energy efficiency opportunities in yarn production

## Slide 10: MOISTURE MANAGEMENT - 3X DRY
3XDRY technology from Schoeller
I. Energy efficiency opportunities in yarn production

## Slide 11: WEAVING
I. Energy efficiency opportunities in yarn production

## Slide 12
Control Air Leakages in looms
  Leakages up to 15-20% of total air demand have been observed
Optimize compressed air pressure according to yarn count
  Mostly, higher air pressure is provided to cover for pressure loss due to leakages; hence inducing more leakages
Automate the air conditioning parameters based on real- time temperature, and humidity
  Don’t forget to adjust air changes according to number of machines operating in the area; and temperature and humidity conditions
Maintain Air Balance among Supply and Return air
  Maintaining positive displacement (~3-5%) facilitates fluff removal from air, reducing fluff accumulation in the looms hence maintaining energy performance
Production Planning
  Improve machine up-time to improve energy performance
Common Air Leakages in Air Jet Looms
Relay Valve
Tuck Inn
Suction Mouth
Pre-winder
Internal PVC Link Pipes
EE OPTIONS IN AIR JET LOOMS
I. Energy efficiency opportunities in yarn production

## Slide 13: II. WET PROCESSING

## Slide 14: WATER SAVING DUPLICATION RULES
II. WET PROCESSING

## Slide 15: WATER SAVING DUPLICATION RULES
II. WET PROCESSING

## Slide 16: II. WET PROCESSING
Automatic steam control valves in the desizing, dyeing, and finishing of denim fabric
The recovery of condensate in wet-processing plants
Utilization of heat exchangers for heat recovery from wet-process wastewater
Power factor correction
Using water economically in factories
Components in steam system:
  Steam traps
  Factors affecting boiler efficiency
  Heat recovery systems
  Waste heat recovery system
  Energy consumption
POTENTIAL FOR OPTIMIZATION AND PERFORMANCE IMPROVEMENT

## Slide 17: II. WET PROCESSING
SINGEING
Methods
Direct Flame application on fabric
Passing fabric over a Heated Copper Plates/rollers
Energy Efficiency Options
Controlling flame size and fabric roll speed
Variable Flame Width
Improve burner efficiency
Recover and reuse cooling water
Parameter | O2 | CO | NOx | NO | NO2 | CO2 | SO2 | Flue Temp.
 | % | ppm | ppm | ppm | ppm | % | ppm | ◦C
Standard (PEQs) |  | 649 | 195 |  |  |  | 603 | 
New Singeing Machine | 19.22 | 145 | 1.2 | 0 | 1.2 | 0.99 | 0 | 139

## Slide 18: II. WET PROCESSING
DE-SIZING
If Singeing is done, De-sizing is conducted in the Singeing Quenching batch
Methods vary according to size applied
Enzymatic (Process control!; for starched based sizes)
Oxidative (usually for different types of textiles, applying hydrogen peroxides, caustic soda) –
Rarely used
Use of acids (sulfuric or hydrochloric acid)
Washing out with hot water and wash soda
Energy Efficiency Options
Waste water heat recovery
Improving Insulation of Hot Water Baths
Optimizing process using pH, temperature and speed with automation

## Slide 19: II. WET PROCESSING
BLEACHING
Common methods
Hydrogen peroxide (H2O2)
Sodium hypochlorite
(chlorine bleaching lye, NaClO)
Sodium chlorite (NaClO2)
Sulphur dioxide (SO2)
Energy Efficiency Options:
Waste water heat recovery (~6m payback)
Improved heat exchanger material (e.g. Stainless Steel) allowing longer life and reduced corrosion; hence improving heat exchanger efficiency

## Slide 20: II. WET PROCESSING
MERCERISING
Refining process with the aim of improving tensile strength, dimensional stability and improved absorbency for consequent dyeing
Methods
Sodium hydroxide bath with heat treatment under tension or without tension, then neutralization with an acid plus washing
Ammonia (very rare)
Energy Efficiency Options
Optimizing steam in-take of Drying Rollers: vendors claim ~14% steam saving but its not verifiable; companies have experienced improvement in process quality and control
Waste water heat recovery
Caustic Recovery (shown on next slide)
Reusing Mercerising wastewater in scouring

## Slide 21: II. WET PROCESSING
NaOH is re-used in Mercerising (24 – 30 Baume)
H2SO4 consumption is reduced at Effluent Treatment
Hot water available to feed into the processes – saving steam
Return on Investment ~ 3 years
RECOVERING NPOS – CAUSTIC RECOVERY PLANT

## Slide 22: II. WET PROCESSING
Hydrogen peroxide bleaching
Most common process for cotton
Takes 2-5 hours at 75-100° Celsius
Requires “clean up”
Can weaken tensile strength of material
Enzyme bleaching: More Sustainable
Discoloration can be achieved in 60 minutes
High temperatures not required
Reduced Caustic Soda consumption for combined scour and bleaching. (zero alkali for scouring)
Salt concentration in effluent reduced
Less rinsing required
Combo Bleaching
Bleach Clean-up
PRE-TREATMENT

## Slide 23: II. WET PROCESSING
Plasma Treatment
Cadira Process from DyStar
SUSTAINABLE PROCESSING TECHNOLOGY

## Slide 24: II. WET PROCESSING
Using low TDS water for dyeing and post dyeing operations helps reducing
  Dyes, chemicals and auxilliary consumption
  Process time
  Liquor Ratio
Improved heat exchanger material (e.g. Stainless Steel) allowing longer life and reduced corrosion; hence improving heat exchanger efficiency
Low Liquor Ratio and use of high fixation dyes helps reducing
  Steam consumption
  Water pumping cost
  Process time  electrical energy
Improve insulation of machine
Waste water heat recovery
  Additionally, an insulated hot water storage tank might also be needed if hot water is to be used in process
Cooling water recovery and reuse
ENERGY EFFICIENCY OPTIONS IN DYEING

## Slide 25: II. WET PROCESSING
SWITCHING TO COLD PAD BATCH (CPB) INSTEAD OF CONVENTIONAL REACTIVE DYEING
It is not possible to switch to cold pad batch dyeing for every reactive dyeing setup (High precision and control required)
However the associated benefits encourage the textile mills to put in more efforts
  Up to 50% energy consumption reduction
  Up to 50% water consumption reduction and reduced wastewater
  No use of salt, reducing the pollution load of generated wastewater
  The fabric don’t undergo abrasion so dyed fabrics have smoother surface

## Slide 26: II. WET PROCESSING
Criteria | Rs / 100 Kg | Production T/day | Relative Cost
Blind Dyeing | 3,000 | 1 | 100
Dyeing + Sampling (If Shade is OK) | 3,145 | 0.92 | 105
Dyeing + 1 addition (Same Bath) | 3,513 | 0.74 | 117
Dyeing + 1 addition (Fresh Bath) | 4,000 | 0.63 | 134
Dyeing, Drying & Redyeing (Correction) | 4,974 | 0.54 | 166
Dyeing, Stripping & Redyeing | 5,658 | 0.53 | 189
Dyeing, Drying & Black Over Dyeing | 6,500 | 0.45 | 217
Anugraha Fashion Mill P Ltd, Tiruppur
IMPORTANCE OF RIGHT FIRST TIME DYEING..

## Slide 27: II. WET PROCESSING
Older overflow dyeing machines use excessive water for batch dyeing.
Lower-liquor-ratio dyeing machines (air-flow machines) using compressed air instead of water
Reduce the use of water and auxiliary agents.
The liquor bath ratio is only 1:3 or 1:4, compared to older machines 1:8 or even 1:12.
Air-flow, even-flow, and other low-liquor-ratio dyeing machines can save
Around 50 percent of water,
Around 15 percent of steam, and
15 to 50 percent of auxiliary agents used during dyeing,
Saving 2 to 3 hours of production time per vat.
LOW-LIQUOR-RATIO DYEING

## Slide 28: II. WET PROCESSING
In order to get very, very low liquor ratio’s some machine manufacturers have developed machines that use a winch reel in combination of a high pressure jet of air to drive the fabric ropes around the machine.
The dye liquor is sprayed onto the fabric in a fine mist as it exits the jet mechanism
The lowest liquor ratio on the market:
man-made fibres approx. 1:2,
natural fibres 1:3 to 1:4, depending on the article and structure.
This AM-ICD is equipped with a conveyer to transport fabrics which enables it to achieve its extremely low MLR.
AM-ICD hybrid machines eliminates the need to have separate dyeing machines for cotton and polyester
LOW MLR (MATERIAL LIQUOR RATIO) MACHINES – AIR JETS

## Slide 29: II. WET PROCESSING
Dyes dissolves naturally
Polymer fiber swells results in easy dye diffusion
Ensures deep penetration
Effective coloration of hydrophobic polymers.
CO2 dyeing of PES and PP fibre is already developed on an industrial scale
CO2 has the advantage over other gases of being non-flammable, non-explosive and non-toxic.
WATER FREE DYEING

## Slide 30: II. WET PROCESSING
https://news.nike.com/news/nike-colordry
Ecological Benefits (compared to water dyeing ) | Dyeing With CO2 Ecological Benefits / Dyes
No Water Usage No Waste Water Up to 50%-75% less CO2 emissions No Chemicals | 
WATER FREE DYEING – NIKE & DYECOO

## Slide 31: II. WET PROCESSING
Fibres are extruded with pigments already included, so no separate dyeing step is required
Color is incorporated throughout the fibre
Such color fibre are resists chemicals, bleach and even sun-fading
SUSTAINABILITY APPROACHES: SOLUTION (DOPE) DYEING

## Slide 32: II. WET PROCESSING
Bio-processing can simply be defined as the application of living organisms and their components to industrial products and processes, which are mainly based on enzymes.
Desizing: amylase, lipase.
Scouring: pectinase, cellulase.
Bleaching: oxidoreductase. xylanase.
Dyeing: oxidoreductase.
Finishing: cellulase, oxidoreductase, lipase.
Composting (biodegradation of textile wastes): cellulase, protease, nylonase, polyesterase.
Delignification, decolourisation of dyes: laccases
Green Chemistry (Chemical Alternative)
GREENER PREPARATION AND DYEING

## Slide 33: II. WET PROCESSING
The Curing chamber is the main area of interest in which air is heated either through direct natural gas firing or indirect air hot thermal oil
  Automation of curing chambers through linking fans and fuel firing with the exhaust moisture and temperature of each chamber
  Heat Recovery from exhaust flue gases
  Insulation of curing chambers
  Digital printing
                Environmentally friendly because it applies printing inks directly onto fabrics and produces no waste.
                It is particularly suitable for factories with small-batch, short-cycle, high-quality, and individualized products.
                It can be used for printing on a wide range of fabrics including cotton, linen, silk, wool, and polyester.
ENERGY EFFICIENCY OPTIONS IN PRINTING

## Slide 34: II. WET PROCESSING
Reduce water consumption and pollution load on effluent stream.
33% of water saving and cost saving of 48% in scouring process.
Higher productivity with an improvement in quality.
Conventionally caustic soda is used to break the pectin layer.
Alternatively pectinase enzymes can be used, which consumes less water and reduces fibre losses.
Pectinase enzyme reacts with pectin and hydrolyses it into soluble products, thus exposing the cellulose underneath.
BIOSCOURING IN PRETREATMENT OF COTTON FABRICS

## Slide 35: II. WET PROCESSING
Recipe | Dosage (g/l) | Temp ( 0c) | Time (min) | Remarks
Dyesofter PL | 1.5 | 95 | 30 | Lubricant
HICLEAN 33 | 1.0 |  |  | Scouring agent
 |  |  |  | Scouring agent
SK-PRA 50 | 1.5 |  |  | Scouring agent
NaOH (45%) | 2.0 |  |  | Alkali
Acetic Acid | 0.7 | 40 | 8 | Neutralization
Water | 3 time /batch |  |  | 
Chemical cost | $0.0246/kg |  |  | 
Running time | 120 min/batch |  |  | 
CONVENTIONAL ALKALI SCOURING PROCESS
Recipe | Dosage (g/l) | Temp ( 0c) | Time (min) | Remarks
Sampol BS | 1.5 | 95 | 10 | Peptidase enzyme
Skoclean SOL | 1.0 |  |  | 
Skoclean SOL | 1.0 |  |  | Scouring agent
Acetic Acid | - | - |  | No need
Water | 1 time /batch |  |  | 
Chemicals cost | $0.0234/kg |  |  | 
Running time | 80 min/batch |  |  | 
NEW BIO SCOURING PROCESS
BIOSCOURING IN PRETREATMENT OF COTTON FABRICS

## Slide 36: II. WET PROCESSING
One stage of a multi stage evaporation plant with a preheater for weak caustic lye
CRP (CAUSTIC RECOVERY PLANT) SYSTEMS

## Slide 37: II. WET PROCESSING
http://www.arvind.com/pdf/ArvindSR.pdf
ZLD (ZERO LIQUID DISCHARGE) SYSTEMS

## Slide 38: II. WET PROCESSING
Osmosis is a naturally occurring phenomenon in which a weaker saline solution tends to migrate to a strong saline solution.
Reverse Osmosis is simply osmosis in reverse.
While Osmosis occurs naturally, to reverse the process there is a need to apply energy to the more saline solution
Osmosis process
Reverse Osmosis process
(RO) SYSTEM FOR RECYCLING OF WASTEWATER

## Slide 39: II. WET PROCESSING
ADOPTION OF COUNTER FLOW MERCERIZATION
Reuse in mercerizing: On the mercerizing range, the scope for water conservation and reuse lies in adopting a countercurrent flow pattern.

## Slide 40: II. WET PROCESSING
AUTOMATIC CHEMICAL DOSAGE SYSTEM
Automatic dosing of dyestuff
Automatic weighing and dosing of liquid chemicals
The following requisites are to be considered a must when planning a purchase and then setting up a good-quality dispensing system: • Reliability
• Speed
• Precision
Benefits:
Improves accuracy from the start, reducing the need for rework.
Saves time, chemicals, water and energy.
Automatic systems reduce pollution and chemical waste.
Creates a safe working environment, free from exposure to toxic chemicals.

## Slide 41: II. WET PROCESSING
Adjust the temperature of the oil furnace/injection nozzle according to the stretching machine requirements (≥ 50°C).
Automate the exhaust gas according to temperature, humidity, fabric feeding speed.
Install frequency converter for ID/FD fan and humidity sensor.
Install exhaust heat recovery system with filter and safety control.
Close the exhaust line when waiting for the stretching machine, optimize batch change.
Plan to reduce machine stoppage, optimize heating/cooling.
Utilize ≥ 75–80% width, clean filter, good insulation.
Interlock the fan with the main machine.
STENTER
Notes: Close exhaust streams during idling in Máy căng
It is common practice to leave the exhaust systems running during the changing of batches, which may take 10 – 15 minutes or more and in some extreme cases (in some commission dyers) could happen every hour.
Since Máy căngs have a large air-heating requirement, it is important, whenever possible, to isolate the exhausts, or at least partially close them during idle periods (Carbon Trust, 1997).
Proper scheduling in finishing minimizes machine stops and heating-up/cooling-down steps and is therefore a prerequisite for energy savings (European Commission, 2003).
Giải pháp tăng hiệu quả năng lượng Điều chỉnh lò dầu truyền nhiệt/mỏ phun khí dựa trên yêu cầu nhiệt độ trong máy căng định hình: Nhiệt độ dầu phải trên 50 độ C Tự động hóa khí thải từ máy căng định hình dựa trên nhiệt độ, độ ẩm và tốc độ nạp vải (feed rate) Cần cài đặt biến tần trên quạt ID/FD và cảm biến độ ẩm vải Lợi ích khác: giảm chênh lệch giữa các sắc thái, từ đó cải thiện chất lượng Hệ thống thu hồi nhiệt từ khí thải Cần lắp bộ lọc hiệu quả trước hệ thống thu hồi nhiệt LƯU Ý: lắp đặt hệ thống điều khiển thích hợp để tránh cháy bộ lọc Đóng đường xả khi ở chế độ chờ cho Máy căng Thông thường nên để các đường xả hoạt động trong quá trình chuyển mẻ vải. Cô lập các đường xả, hoặc ít nhất đóng một phần đóng trong thời gian chờ (Carbon Trust, 1997). Lập kế hoạch sản xuất thích hợp để tối thiểu thời gian dừng máy và các bước gia nhiệt/làm nguội (European Commission, 2003).
Một số giải pháp thường gặp: Sử dụng ít nhất 75 - 80% chiều rộng Làm sạch bộ lọc định kỳ để giữ ổn định hiệu suất sấy. Đảm bảo cửa buồng không bị rò rỉ cũng như cách nhiệt thích hợp cho phía trên, dưới và hai bên. Động cơ quạt gió nên được khóa liên động với bộ điều khiển chính, tức là sẽ dừng khi máy dừng hoạt động

## Slide 42: II. WET PROCESSING
Air to Air Heat Exchanger
Schematic of a Stenter with and without Air to Air Heat Recovery Unit
Source: www.monforts.com
Air to air heat exchangers such as plate heat exchangers, glass tube heat exchangers or heat wheels
Efficiencies are typically around 50 - 60%,
Problems with bypass gas, contamination and corrosion can occur.
STENTER HEAT RECOVERY
Notes: Air to Air Heat Exchanger
The hot stenter exhaust gas at up to 160°C is transported by the existing waste air fansthrough the bare tube heat exchanger into the atmosphere. The cold, clean fresh air(approximately 50% of the waste air volume) is drawn in by the fresh air fan in counter-flowto the waste air, through the heat exchanger and into the stenter. As it passes through the heat exchanger, this air is preheated to approximately 100°C
.
This hot air can be used in the burner of the stenter itself so as to lessen the requirement of fuel in the burner. The only problem is that the burners will have to be modified in order that they are capable of accepting the air at high temperature. This process is illustrated with colour coding in the figure

## Slide 43: II. WET PROCESSING
AIR / WATER SYSTEMS – PRINCIPLE
Notes: Air to Air Heat Exchanger
The hot stenter exhaust gas at up to 160°C is transported by the existing waste air fansthrough the bare tube heat exchanger into the atmosphere. The cold, clean fresh air(approximately 50% of the waste air volume) is drawn in by the fresh air fan in counter-flowto the waste air, through the heat exchanger and into the stenter. As it passes through the heat exchanger, this air is preheated to approximately 100°C
.
This hot air can be used in the burner of the stenter itself so as to lessen the requirement of fuel in the burner. The only problem is that the burners will have to be modified in order that they are capable of accepting the air at high temperature. This process is illustrated with colour coding in the figure

## Slide 44: II. WET PROCESSING
DRYING PROCESS
Modulate steam pressure according to process temperature requirement (Shade, fabric weight, batch size etc.) to optimise steam use
  Majority companies don’t even install Steam Pressure Reducing Valves with dryers and all dryers are provided same pressure
Install electric, high-pressure blowers, with adjustable nozzles, instead of using compressed air
Assess possibility of recirculating the machine exhaust air
  This would require installing a fluff collector Jute bag (like used in Carding Machine filters in Spinning industry) and adding 30~40% fresh air
  May result in better heat exchange as well as reduction in process time and Steam consumption
Notes: Air to Air Heat Exchanger
The hot stenter exhaust gas at up to 160°C is transported by the existing waste air fansthrough the bare tube heat exchanger into the atmosphere. The cold, clean fresh air(approximately 50% of the waste air volume) is drawn in by the fresh air fan in counter-flowto the waste air, through the heat exchanger and into the stenter. As it passes through the heat exchanger, this air is preheated to approximately 100°C
.
This hot air can be used in the burner of the stenter itself so as to lessen the requirement of fuel in the burner. The only problem is that the burners will have to be modified in order that they are capable of accepting the air at high temperature. This process is illustrated with colour coding in the figure

## Slide 45: Cleaning by blowing air creates a special effect
Install an electrically powered and high-pressure blower, with customizable nozzles, instead of using compressed air Calculation example: 03 pipes with an inner diameter of 4mm in each area Gas consumption = 94 m3/hour/working station Cost savings/workstation = ~$6,000/year Cost for an electric, high-pressure blower = $500 Payback = immediate

## Slide 46: Maintenance Preventive Maintenance
This is an action taken over time or based on a machine schedule, detecting or eliminating the degradation of a device or system with the aim of maintaining or extending its useful life to an acceptable level.
Advantage:
Increase the life cycle of the device. Flexibility in adjusting maintenance cycles. Reduce equipment or process failures and estimate cost savings of 12% to 18% compared to corrective maintenance programs.
Shortcoming:
Skilled workers are needed. Add some unnecessary maintenance activities. There is the potential for accidental damage to the equipment if unnecessary maintenance is carried out.

## Slide 47: III. EE opportunities in garment production

## Slide 48: 1. EEMs FOR SEWING MACHINES
Advantages: No energy loss, smooth operation with low noise, Better speed control
Energy Efficiency:
Using servo motors for sewing machines can help save 60–80% of electricity consumption compared to traditional motors.
Average investment cost: VND 1.8 million – 3 million per motor.
Due to relatively low electricity prices in Vietnam, the payback period for this solution is typically 2–5 years.
In many cases, in addition to saving electricity, servo motors also help increase productivity thanks to their higher operating speed.
      Servo Motor
Load Profile Graph – Traditional Sewing Machine Motor
Load Profile Graph – Servo Motor

## Slide 49: 2. STEAM IRON HEAT RECOVERY
Practice | Energy Saving | Typical Pay Back Period
Steam Iron Heat Recovery | 10 – 30% | 8 months to 1 year
Steam savings can be achieved through a series of measures
Improved steam pressure regulation.
Orifice installation.
Insulation.
Heat recovery.

## Slide 50
Using the steam trap for the irons
Replace the centralized steam system with a decentralized system using electricity
3. SAVING STEAM FOR IRONS

## Slide 51: 4. DENIM WASHING TECHNIQUES
Mechanical wash
Chemical wash
Tumbler washing Machines
Rotary Drum Washing Machines

## Slide 52: 5. OZONE WASHING SYSTEM
Ozone having bleaching property, hence can be used for bleaching of denim.
Ozone allows washing to be conducted using cold water, thereby saving considerable heat energy and water consumption.
Enhances the wash process, resulting in a significant reduction in detergent dosage and number of rinses, thus saving water.
Gentler to fabrics, thus extending linen life.
Ozone gas also use for localized facing.
Beneficial for effluents, resulting in reductions in COD
Mist Spray Technology (Fabcare – Mist Spray – Resinator):
Applied to fabric finishing: softening, dyeing, antibacterial...
Environmentally friendly, cost-saving.
Reduces 90% water, 47% energy, eliminates chemical waste.

## Slide 53: 6. NANO BUBBLE TECHNOLOGY IN SUSTAINABLE JEAN FINISHING

## Slide 54: 7. RESOURCE EFFICIENT PROCESSES IN GARMENT WASHING
The pumice stone with an abrasive drum coating, fastened to the internal drum of the washing machine which can create a number of ﬁnishes through ﬂexible abrasion adjustments.

## Slide 55: 8. SUSTAINABILITY APPROACHES: LASER TECHNOLOGY
  Laser. Computer-driven laser technology can replicate localized wear, whiskers, and intricate lacelike patterns without water, chemicals or stones.
Costly, each garment must be individually positioned for treatment, and only one side can be treated at a time.
Excellent for localized effects, laser is less beneficial for overall bleaching.

## Slide 56: 9. FLEXIPRO LASER MACHINE FOR DRY PROCESS
Patented Ultra fast scan (UFS) technology increases marking speed and takes spot accuracy to a higher level
Artificial vision camera: Allows a perfect positioning, placement of garment
3D Optical system: Automatically modifies the spot diameter : better definition, thinner lines, more grey scale
Benefit:
Increase the productivity capacity and optimization of costs
Multiplies the possibilities of design and creativity
Precise control of real-time production of machines
reduction of water consumption, energy and chemicals.

## Slide 57: 10. PRODUCTIVITY IMPROVEMENT BY MANAGEMENT
R&D, work study and hourly Operator Performance Check
Following Systems such as 5S and Kaizen
Select suitable line layout, Improve Line Balancing
Reduce Line Setting Time, Eliminate Idle Time
Using UBT Sewing Machine (Under Bed Trimmer) , and Work Aids
Continuous Feeding to the Sewing Line
Feed Fault Free Garment Components to Line
Skilled training to Sewing Operators
Inline Quality Inspection at Regular Interval
Give Pleasant Working Environment, Operator Motivation
Use ERP Software’s
Notes: Work aids are Additional devices that can be added to basic sewing machines such as folders, guides and pressure foots. If work aids are used effectively operation cycle time can be reduced many fold than existing cycle time.

## Slide 58: Discussion
Fill out the following comparison table:
EEM | Investment costs | Energy Saving Efficiency (%) | Feasibility | Application notes (suitable for which stage)
Low Density Dyeing Machine |  | 30–50% |  | 
Wastewater heat recovery |  | 15–25% |  | 
Automated chemical dosing |  | 5–10% |  | 
Steam system insulation |  | 10–15% |  | 
Compressed air control (reduced leakage) |  | 8–12% |  | 
Digital Printer Replaces Mesh Printing |  | No water waste, no chemical reduction |  | 

## Slide 59: Discussion
Divide into groups of 4–6 people, discuss afterwards, and then each group presents 3–5 minutes. Encourage each team to draw diagrams, quick spreadsheets, or share practical experiences that are appropriate to the content of each question
1. What energy-saving solutions has your factory applied in the stages (yarn, weaving, dyeing, finishing, sewing, ...)
Energy Efficiency Assessment Financial Performance Assessment Scalability Assessment
2. Calculation: Preliminary estimate of the savings if applying a solution learned today (e.g., using a low-capacity dyeing machine, installing a servo for a sewing machine, recovering wastewater heat, etc.). 3. According to your group, what is the biggest barrier when implementing energy saving in your business? How to fix?

## Slide 60
THANK YOU