## Slide 1: TRAINING PROGRAMME FOR INDUSTRIAL ENTERPRISEs
Module 8.7:
Energy efficiency opportunities in seafood production lines
Technical staffs

## Slide 2
System and equipment of seafood processing factories Solutions for freezing systems Solutions for cold storage, flake ice Solutions for Refrigeration Compressors Solutions for condensers Other Solutions
CONTENT

## Slide 3
The most important energy use processes in the frozen seafood processing process include:
  Processing and raw material handling equipment Refrigeration system HVAC Hot water Pump/Fan Compressed Air Light
1. SYSTEM, EQUIPMENT OF SEAFOOD PROCESSING FACTORIES

## Slide 4
The refrigeration system accounts for 70% - 75% of the total electricity consumption of the aquatic plant. In particular, the freezing system (as part of the refrigeration system) is the largest electricity consumer, accounting for 35–55% of total consumption.
Fish Processing
Shrimp Processing
Wastewater Treatment
4%
Other 11%
Freezing48%
Light
4%
Air conditioning
7%
Cold water
3%
Flake ice
10%
storage 10%
Water Supply
3%
Other 9%
Air conditioning
4%
Flake ice
17%
Storage
8%
Freezing50%
Hot water 3%
Wastewater Treatment
3%
Water Supply
4%
Light
2%
1. SYSTEM, EQUIPMENT OF SEAFOOD PROCESSING FACTORIES

## Slide 5
The refrigeration system of the factory includes refrigeration compressors, freezing equipment (IQF, CF, ABF), warehouses, rocks, etc. In addition, the refrigeration system also has an evaporative condenser (or cooling tower). The refrigerant used is NH3 or R22. Continuous and individual systems. For continuous refrigeration systems, these compressors are divided into 3 systems: -45oC system, -40oC system and -28oC system.
1. SYSTEM, EQUIPMENT OF SEAFOOD PROCESSING FACTORIES
Notes: Theo Nghị định thư Montreal mà Việt Nam là một thành viên, môi chất lạnh R22 chỉ được sử dụng ở mức 2.5% sau năm 2030
Hầu hết các máy nén lạnh của hệ thống lạnh sử dụng môi chất R22 là các thiết bị đơn lẻ vì thế có thể đầu tư dần
Giảm từ 5 đến 10% hiệu suất của hệ thống lạnh dùng R22 ở nhiệt độ vận hành thấp (từ -28 to -45 0C) so với việc sử dụng hệ thống lạnh dùng NH3.

## Slide 6
Do not operate cold storage, flakes with freezing equipment above the same boiling temperature Evaporative Pressure Optimization Limit IQF conveyor belts running idle and underloaded. Proper operation of freezers
2. SOLUTIONS FOR FREEZING SYSTEM

## Slide 7
Don’t operate cold storage / flake ice on the same (low) boiling/evaporating temperature as IQF & other low-temp loads
Separate suction groups into 3 systems: system - 450C, system - 40oC and -28oC system.
=> so each can run at the highest feasible evaporating temperature (Te). Every +1 °C in Te cuts compressor energy roughly 2–4%; separating loads often lets medium-temp circuits run +3–5 °C warmer than low-temp.
~6–20% compressor kWh, depending on how much Te can be raised.
Central refrigeration system principle diagram
2. SOLUTIONS FOR FREEZING SYSTEM

## Slide 8
Evaporative Pressure Optimization:
The installed heat point of the IQF system is very low (-42°C), which is equivalent to the evaporative heat of the refrigeration system of -45°C, while the required temperature at the center of the frozen product is -18°C.
The proposed solution is to optimize the evaporative pressure.
Increase the set temperature of the IQF system to -38°C by setting the indoor unit temperature of the refrigeration system to -41°C. Increase the frequency of IQF defrosting to maintain the temperature of the IQF chamber at -36° C.
2. SOLUTIONS FOR FREEZING SYSTEM
Rules of thumb: 2–4% energy per +1 °C Te or about ~2% per +1 psi suction pressure.

## Slide 9
For every 1°C increase of the evaporation temperature, the energy consumption will decrease by 3%
Increase the evaporation temperature from -10 ºC to -7 ºC by increasing the size of the indoor unit as much as possible, which can save 9% of the energy consumption of the refrigeration compressor.
2. SOLUTIONS FOR FREEZING SYSTEM

## Slide 10
Limit IQF belts running idle/under-loaded
Avoid running empty/freezers; reduce air/fan volume and belt speed when product load is low (VFDs, standby modes). Trials in blast/IQF contexts show fan speed control can cut total freezing-room energy ~10–22%; fan affinity laws mean 50% speed ≈ ~85% fan-power reduction.
d. Proper freezer operation (defrost, doors, setpoints, airflow)
Optimize/shorten defrosts, keep doors/curtains effective, maintain coils/air paths, and tune controls; add VFDs where feasible. Guidance and field data show meaningful O&M savings; defrost optimization and general good practice regularly deliver low-double-digit reductions.
~5–15% (and more when systems start from non-optimized practice).
2. SOLUTIONS FOR FREEZING SYSTEM
Notes: hay đầu tư hầm tiền đông, tăng , giảm số lượng máy nén

## Slide 11
Managing Cold Storage Utilization Managing the arrangement of goods in cold storage Split the cold storage if the full load factor is low Using LED Lights Priority is given to stone communes at off-peak hours Producing cold water instead of using flaky ice as cold water Operating stone mortars waving at off-peak hours Cold water supply to the stone mortar
3. SOLUTIONS FOR COLD STORAGE AND FLAKE ICE
Notes: kho lanh chiem 8 -10%

## Slide 12
Managing Cold Storage Utilization:
  Close the warehouse door when no people or vehicles pass by. Installing automatic doors, the potential to save about 10% - 15% of the total electricity consumption of cold storage
3. SOLUTIONS FOR COLD STORAGE AND FLAKE ICE
Notes: kho lanh chiem 8 -10%

## Slide 13
b. Optimizing Arrangement of Goods (FIFO, compact storage): Improve space utilization, minimize door openings, and reduce thermal load. ~20% potential reduction in cooling load from improved layout and fewer door cycles
3. SOLUTIONS FOR COLD STORAGE AND FLAKE ICE
Notes: kho lanh chiem 8 -10%

## Slide 14
Split the cold storage if the full load factor is low: Separate low- and mid-temperature zones so only required sections are live. Combined with utilization improvements, typically 15–30% savings. Switch to LED Lighting: Replace conventional lighting systems in cold storage, which add heat or require extra cooling 70–80% lighting energy savings; also reduces cooling load due to lower heat output
3. SOLUTIONS FOR COLD STORAGE AND FLAKE ICE
Notes: -22 oC, kho lanh chiem 8 -10%
Các nhà máy cá thường chế biến đến 3 giờ
LED giam tải lạnh

## Slide 15
Prioritize Stone/Fish Icing During Off-Peak Hours. Conduct energy-intensive operations during times when electricity is cheaper or when storage load is more available. => ~10–20% reduction in peak energy costs through load shifting
Cold water is produced by putting flaked ice in water tanks. Normally, the COP of the Chiller system will be lower than that of the Chiller system (the evaporation temperature of the medium in the Chiller system is lower). Therefore, the production of chilled water with flaky ice will be less efficient than operating the Chiller system.
The demand for cold water of the factory is about 60 m3/day, the feed water temperature is 27oC, the cold water temperature is 5 oC. In this case, the factory saves a year of 266 million VND for the production of flake ice.
The higher the cost savings when the demand for cold water of the plant is greater.
3. SOLUTIONS FOR COLD STORAGE AND FLAKE ICE

## Slide 16
Produce Cold Water Instead of Flake Ice: Use chilled water reservoirs or cold glycol systems instead of energy-intensive flake ice, which has higher production and storage overhead. => Energy savings vary, but hybrid systems can achieve >10% overall thermal efficiency improvements.
3. SOLUTIONS FOR COLD STORAGE AND FLAKE ICE
g. Operate Stone Mortars (Ice Crushers) in Off-Peak: Shift crushing/mixing to off-peak to reduce electrical rate and thermal load during peak periods.
5–10% energy cost reduction through timing optimization.
h. Use Cold Water Supply for Stone Mortars: Supply cold water directly for cooling needs instead of producing or using flake ice => ~10–15% energy savings due to lower mechanical and pumping energy compared to ice processing and handling.

## Slide 17
4. SOLUTIONS FOR REFRIGERATION COMPRESSORS
Install the inverter for the compressor if necessary. Replace the low-efficiency compressor with a higher-efficiency compressor. Do not allow compressors to run underloaded

## Slide 18
Install the inverter for the compressor in case of necessity:
  The existing refrigeration system is old and is equipped with a manual control system. The refrigeration system has changed from the original design (more refrigeration compressor units). The refrigeration compressor is controlled off/on or manually controlled Screw refrigeration compressors are operated at low load (usually approx. 60 – 80% of capacity) Fixed push/suction pressure is applied.
4. SOLUTIONS FOR REFRIGERATION COMPRESSORS

## Slide 19
Energy consumption remains relatively high when adjusting the power for example at 50%:
Sliding valve control: 71% of power consumption VFD Control: 56% Ideal Performance: 50%
Comparison of the energy consumption of different control measures (for screw refrigeration compressors)
4. SOLUTIONS FOR REFRIGERATION COMPRESSORS
30–50%, per industry data on inverter vs conventional compressors

## Slide 20
Replace a low-efficiency compressor with a higher-efficiency compressor.
  The biggest investment solution in seafood freezing plants is to retrofit the refrigeration system by replacing the Piston refrigeration compressors with screw compressors. The investment rate of this solution is about 150,000 USD/unit for a compressor with a capacity of 250 kW. The payback period is about 5 -7 years => system-level compressor savings estimated in the 10–15%
4. SOLUTIONS FOR REFRIGERATION COMPRESSORS

## Slide 21
Do not allow compressors to run unloaded:
Operate compressor units according to the number of dynamic feeders in operation.
  The energy efficiency of the compressor (screw type compressor type) can be reduced by 20- 30% when operating in non-load mode.
4. SOLUTIONS FOR REFRIGERATION COMPRESSORS
Notes: Thiết bị làm lạnh đã thay đổi so với thiết kế ban đầu (nhiều tổ máy hơn)

## Slide 22
5. SOLUTIONS FOR CONDENSER
Install additional solenoid valves to discharge non-condensing air one by one to reduce the condenser pressure and reduce the electricity consumption of the compressor.
  Savings of approximately 3 – 6% for refrigeration compressors Every 1°C increase in condensate pressure : 1% reduced cooling capacity 3% lower COP

## Slide 23
Installing additional gas and water separation equipment for refrigeration systems:
Many refrigeration systems in frozen seafood processing lines are very poorly maintained. Therefore, there may be damage due to water present in the NH3 solution:
  Increased energy consumption Reduced cooling capacity Lower evaporator pressure at the same temperature Leaks caused by O-shaped hoses and other hoses are fragile Wear and tear of valves and control devices
5. SOLUTIONS FOR CONDENSER
~10–15% energy savings and improve overall system performance and reliability
Notes: Cứ mỗi 1% nước có trong môi chất lạnh NH3, năng suất lạnh suy giảm đi 2% và điện năng tiêu thụ tăng thêm 1%.

## Slide 24
Conversion of some refrigeration equipment using R22 to NH3.
  According to the Montreal Protocol, of which Vietnam is a member, R22 refrigerant will only be used at 2.5% after 2030. Most refrigeration compressors of refrigeration systems using R22 medium are single units so you can invest gradually 5 to 10% reduction in the efficiency of R22 refrigeration systems at low operating temperatures (from -28 to -45 0C) compared to NH3 refrigeration systems.
6. OTHER SOLUTIONS

## Slide 25
Replace fluorescent lamps (T8-magnetic ballasts) with high-efficiency luminaires (LED/T5 lamp)
Type | Power | % Savings
T8 lamp + ferromagnetic ballast | 46 W | -
T5 lamp + electronic ballast | 28 W | 39%
LED | 19 W | 59%
170,000 VND/pcs Payback period within 1.5 years
250,000 VND/pcs Payback period of 3 years
6. OTHER SOLUTIONS

## Slide 26
Wastewater treatment: Install a DO (dissolved oxygen concentration) transducer and inverter for the air pump to control the gas supply to the aerobic tank => around 10% energy saving
6. OTHER SOLUTIONS
Notes: Nếu có không khí trong hệ thống, thì nó chiếm chỗ trong dàn ngưng tụ, làm giảm hiệu quả
trao đổi nhiệt bề mặt.
Kim đồng hồ rung mạnh, áp suất ngưng tụ cao bất thường

## Slide 27
Solar hot water: hot water production => 50–80% lower compared to electric heaters
Heat recovery from hot gas: Recover waste heat from the refrigeration system to produce hot water for seafood washing. The benefits of waste heat recovery can help produce hot water at low energy costs, while reducing excess heat load on the condenser, thus helping the refrigeration system operate more efficiently. => around more than 10% system energy reduction
6. OTHER SOLUTIONS
Notes: Nếu có không khí trong hệ thống, thì nó chiếm chỗ trong dàn ngưng tụ, làm giảm hiệu quả
trao đổi nhiệt bề mặt.
Kim đồng hồ rung mạnh, áp suất ngưng tụ cao bất thường

## Slide 28
Building an energy management system.
Benefits of an Energy Management System:
Reduce energy costs more than 10% Increase production capacity and Product Quality Improving competitiveness Improving the environment and safety Image Promotion Reducing greenhouse gas emissions Compliance with the law
Energy cycle from energy efficiency with a sustainable energy management system
6. OTHER SOLUTIONS

## Slide 29: DISCUSSION
The trainees worked in groups, discussed:
Energy-saving solutions that can be applied at businesses Propose other energy-saving solutions Duration: 15 minutes

## Slide 30
THANK YOU