## Slide 1
Module 9.4:
Typical case study and report on EE in paper and pulp industry in Vietnam
MANAGEMENT OFFICERS
TRAINING PROGRAMME FOR INDUSTRIAL ENTERPRISEs

## Slide 2: Small group discussion and presentation
The case study of your work in energy efficiency has been divided into 03 groups. Each group will prepare a presentation of their findings within 15 minutes. The presentation should include the background of the company, its current status, the equipment used, the process followed, a comparison of the results before and after, and a financial assessment.
Each group will present their findings to the entire class for a 10-minute presentation.

## Slide 3: Case Study for VINAPACO
  Established in 1976
  In Phong Chau commune, Phu Ninh district, Phu Tho province
  Output:
  Pulp: 68,000 tons/year
  Paper: 100,000 tons/year

## Slide 4: CHP cogeneration system at VINAPACO
Boiler | Fuel | Designed capacity/operating tph | Pressure and steam temperature | Comment
Fluidized Bed | Coal Antraxit | 145/90 | 62/450⁰C | Technology in 1970
Black Liquor Recovery Boiler | Black liquor | 36/16-20 | 62/450⁰C | Technology in 1970
Step grate biomass boiler | Bark, sawdust | 20/16 | 13 bar | Technology from China in 2017
Turbines | Unit | Back-pressure turbine | Condensing Turbine
Input steam flow (tph) | Tph | 95 | 85
Input steam temperature | ⁰C | 450 | 450
Input steam pressure | Bar | 62 | 62
Extraction steam pressure | Bar | 13 | -
Extraction steam flow | Tph | 15 | -
Output steam pressure | Bar | 4,5 | -0,85
Output steam flow | Tph | 80 | 85

## Slide 5: Current Status of VINAPACO
Problems:
  The coal-fired boiler is out of date, has low efficiency, and operates at a lower capacity than designed.
  VINAPACO's future strategic plan is to invest in a new production process, which requires a larger amount of steam.
  VINAPACO has a large supply of biomass at a low price, which can be used to produce steam.
VINAPACO's plan:
  Replace the coal-fired boiler and back-pressure turbine for a new CHP system.
  Renovate the steam system and recover condensate.
  VINAPACO has not yet decided on a specific CHP, but the purpose of using CHP for a backpressure turbine is similar to the inlet temperature and pressure of the old boiler.
  However, with recent technology, higher steam temperatures and pressures should be applied.

## Slide 6: Propose to change CHP
Boiler | Fuel | Designed capacity/operating tph | Pressure and steam temperature | Comment
Fluidized Bed | 70% biomass; 30% sub-bitum coal | 120 | 62/450⁰C or 100/510oC | VINAPACO proposed. BEM team proposed
Black Liquor Recovery Boiler | Black liquor | 36/16-20 | 62/450⁰C | Technology 1970
Step grate biomass boiler | Bark, sawdust | 20/16 | 13 bar | Technology from China, 2017
Turbin | Unit | Back-pressure turbine, proposed by VINAPACO | Back-pressure turbine, proposed by BEM
Input steam flow (tph) | Tph | 120 | 120
Input steam temperature | oC | 450 | 510
Input steam pressure | Bar | 62 | 100
Extraction steam pressure | Bar | 13 | 13
Extraction steam flow | Tph | 40 | 40
Output steam pressure | Bar | 4,5 | 4,5
Output steam flow | Tph | 80 | 80

## Slide 7: Comparison of 3 case studies of CHP
Description | Unit | Current coal-fired combined heat and power generation | Combined Heat and Power proposed by VINAPACO | Recommendations from BEM consultants
Fuel demand | MJ/hour | 420.307 | 511.979 | 526.584
Steam in production | MJ/hour | 424,466 | 523.418 | 538.396
Steam energy turned into electricity | MJ/hour | 46.104 | 55.254 | 69.054
Steam available for production line | MJ/hour | 297.843 | 363.514 | 364.659
Thermoelectric cogeneration efficiency | % | 81,83 | 81,79 | 82,36
Power generation efficiency | % | 10,97 | 10,79 | 13,11
Calculate fuel costs | kVNĐ/hour | 23.003 | 20.889 | 21.634
electricity generation capacity | kW | 12.807 | 15.348 | 19.182
subsidized electricity costs | kVNĐ/hour | 23.052 | 27.627 | 34.527
Number of working hours/year | hour/year | 7200 | 7200 | 7200
Reduce annual electricity costs | million VNĐ/year | 165.974 | 198.914 | 248.595
 | $ | 7.062.710 | 8.464.424 | 10.578.515

## Slide 8: Financial Assessment
The proposal for a cogeneration system with steam parameters has higher pressure and temperature was selected for further study on financial evaluation.
Based on the preliminary calculation of the steam system for CHP, a request for quotation was sent to several suppliers including: Vynvke Clean Energy Technology Company; Enesco Jsc; KPN Green Energy Solutions Company Limited; Thermax Limited; Martech Company Limited.
Time to prepare quotation is quite long to get an answer and currently, only Enesco Jsc and Martech Jsc have given an answer for the investment cost like Turnkey Cost (CAPEX) for the CHP system.
The BEM team also sought the help of Power Engineering Consulting Company 1 (PECC1) to simulate the CHP system using Thermo flow software to calculate the details of the CHP system with cost estimation. Three values ​​are used for financial evaluation for the case study.

## Slide 9: The investment and operational costs of a CHP for a typical case
Company | Investment Cost (mil. USD) | USD/MWe net | Operation Cost (million USD)
ENESCO | 23.5 ± 20% | 1,437 | 7.40
Martech | 36 | 2,200 | 7.60
PECC1 | 44.7 | 2,730 | 7.98
Turnkey Investment Cost
Operating cost calculation method for VINAPACO
Costs | Unit | Unit cost (mVND) | Unit number/year | Total (mil VND/year)
Human Resource | Full time work | 120 | 30 | 3,600
Maintenance cost | % of capex equipment | 378,700 | 2.5% | 9,468
Electricity | kWh | 1613 VND | 10,598,055 | 17,094
Coal (30% of fuel) | ton | 1.10 | 50,057 | 55,062
Biomass (70% of fuel) | ton | 0.45 | 116,799 | 52,559
Water | m3 | 0.02 | 198,900 | 3,978
Total |  |  |  | 148,479
Contingency |  |  | 20% | 
Total OPEX |  |  |  | 170,113

## Slide 10: Hypotheses for economic evaluation
 | Amount emitted | Unit cost | Million VND/year | USD/year
Electricity | 95,382,495 kWh | 1,613 VND/kWh | 170,935 | 7,431,968
Boiler | 780,000 ton steam | 380,000 VND/ton | 296,400 | 12,886,957
 |  |  | 467,335 | 20,318,925
Cost of energy generated by CHP
Hypotheses for economic evaluation
Items | Unit | Value | Note
Backup rate | % | 10 | assumption
Equity | % | 30 | 
Loan capital | % | 70 | Maximum loan ratio (HD bank recommended)
Interest rate | % | 10 | Interest rates for commercial loans (HD Bank)
discount rate | % | 14.5 | Reflecting the weighted cost of capital, assuming 70% debt at 10% and 30% equity with a return on equity of 25%
Tax rate | % | N/A | Corporate tax rates - all calculated according to EBITDA
Electricity price | VND | 1613 | 24 hour average price for 110kv connections

## Slide 11: Economic analysis results for typical case
Summary | NPV | IRR | Payback Period
Enesco | $ 23,252,914 | 39% | 2.53
Martech | $ 6,454,649 | 19% | 4.58
PECC1 | $ -6,961,755 | 10% | 5.59
Chart: Ginter triagle levelised cost of electricity and steam
| 445.68841259169074 | 0
Ginter ENESCO | 0 | 3280.1959
Ginter Matrec | 0 | 4096.1184
PPEC | 0 | 4525.229
Steam cost | 0 | 2000 | 6000
Electricity cost | 1612.8929 | 1612.8929 | 1612.8929

## Slide 12: Discussion
Q & A of the case above

## Slide 13: Conclusion for the case study
Ginter's triangle is an approach to the separation of electricity and heat costs proposed by the Russian Engineer - L.L. Ginter. A triangle is developed in the space between two axes - the costs of electricity and heat. The triangle allows estimating the unit price of the second product assuming the unit price of the first product.
The quotes received differ significantly, reflecting many unclear information when requesting a quote. Therefore, it should be considered a preliminary estimate and further research is required to obtain a detailed request for quotation with clearer technical specifications.
However, based on this initial assessment, a cogeneration system is feasible when the CAPEX is ~$36 million or less - in which case both steam and electricity production can be lower than the price of ESCO steam and EVN electricity

## Slide 14: Conclusion and Recommendations
Pulp and paper is a circular industry that can recover up to 80% of its used products.
This industry is heavily dependent on imported scrap as raw material and has difficulties in managing imported scrap.
This industry depends significantly on imported scrap and raw materials and has difficulties in managing imported scrap.
High energy costs in production costs. Boilers and steam systems are the main sources of thermal energy consumption in the industry.
The use of biomass boilers for steam generation or CHP cogeneration systems is a viable bioenergy opportunity in the industry. A reliable supply of biomass fuel is crucial for the decision to install a boiler.
The ESCO steam trading model should play an important role in encouraging the application of biomass boilers in the industry.
VINAPACO is a good case study for CHP cogeneration using biomass as the main fuel. However, further research is needed to obtain detailed calculations for the CHP cogeneration system of the plant.

## Slide 15
Thank you!