## Slide 1: TRAINING PROGRAMME FOR INDUSTRIAL ENTERPRISEs
Module 4.7:
Current and potential of EE in the seafood industry in Vietnam
MANAGEMENT OFFICERS

## Slide 2: OBJECTIVES
Understanding the current situation and potential for energy savings in Vietnam
Understanding the current situation and potential for energy saving in the plastics industry in Vietnam

## Slide 3: BREAK INTO GROUPS AND DISCUSS
Divide the class into 4 groups
15-minute discussion
In your opinion, which industry uses the most energy in Vietnam?
What is the main source of energy does your company use?
Identify the main energy-consuming areas/equipment and have the potential for natural resources in the seafood processing industry?
What are the energy savings opportunities in your company?
Present in 5 minutes

## Slide 4: GLOBAL INDUSTRIAL ENERGY USAGE
Total Final Energy Consumption (TFC) by Sector from 1990 to 2020-2022
Notes: OECD Europe includes: Austria, Belgium, Czech Republic, Denmark, Finland, France, Germany, Greece, Hungary, Iceland, Ireland, Italy, Luxembourg, the Netherlands, Norway, Poland, Portugal, Slovakia, Spain, Sweden, Switzerland, Turkey, and the United Kingdom.
Changing focus from the U.S. stage of energy management to the work stage now.
Borrowed this slide from DOE. The stand out part of this is that industry consumes 50% of world energy. When you look at many developing countries, industrial energy use can be as large as 70- 80% of their total use.
This does not go unrecognized. Many countries have developed energy management system standards or other types of national programs to help their industry. These countries include Denmark, Ireland, China, Korea, Japan, Spain, Thailand, Germany, Sweden, United Kingdom. So there is a ground swell of energy management standards that have been developed our are in the process of being developed.

## Slide 5: FINAL ENERGY CONSUMPTION BY INDUSTRY IN VIETNAM
Transportation
31,7%
Services
3,9%
Household 14,9 %
Non- energy
2%
Industry
45,7%
Argriculture
1,8 %
2012
2021
Industry
Non- energy
5,5%
Argriculture
5,2%
Transportation
16,7%
Services
3,2%
Household
15,3 %

## Slide 6: CURRENT STATUS OF ENERGY USE IN VIETNAM
Agriculture, forestry and fisheries
Construction
Industry
Non- energy
Household
Services
Transportation

## Slide 7: CHARACTERISTICS OF ENERGY CONSUMPTION IN VIETNAM’S INDUSTRY
The industry is the leading energy consumer sector in Vietnam, based on electricity consumption and final energy consumption
Vietnam currently has 3,491 (in 2023) DEUs (up from 2496 establishments since 2017) consuming 51,393,648 TOE, of which 2,864 DEUs in the industrial segment account for the majority, consuming 40,586,299 TOE. Vietnam's industry has a great advantage in energy saving.
In which, seafood industry has 80-90 DEUs, represent 3.14% of the total number of DEUs.
By 2025, Vietnam requires 100% of designated energy-using enterprises to implement energy management systems as mandated by Decision 280/QD-TTG from the Prime Minister approving the National Program for Energy Efficiency for the 2019-2030 period.
The application of Energy Management Systems in Vietnam is still limited and weak. Many enterprises only implement these systems to meet legal requirements.

## Slide 8: DEUs
Chart: 
| 2017 | 2018 | 2019 | 2020 | 2021 | 2023
Năng lượng tiêu thụ | 24126 | 26750 | 35997 | 34294 | 51394 | 40586
Số lượng DEU | 2496 | 2605 | 3006 | 2961 | 3068 | 3491
Số lượng CSSD NLTD và năng lượng tiêu thụ tương ứng, giai đoạn 2017-2023
(Nguồn: Tổng hợp từ Danh sách CSSD NLTĐ)
The seafood processing industry has about 80-90 DEUs

## Slide 9: EE TARGETS FOR VIETNAM'S INDUSTRIAL SECTORS BY 2030
Industries | By 2025 |  | By 2030 | 
 | From | To | From | To
Steel industry(%) | 3 | 10 | 5 | 16.5
Seafood process (%) | 5 | 7 | 8 | 10
Chemical industry(%) | 7 |  | 10 | 
Plastic manufacturing industry(%) | 18 | 22.46 | 21.55 | 24.81
Cement(%) | 7.5 |  | 10.89 | 
Textile and Garment(%) | 5 |  | 6.8 | 
Beverages and Beer(%) | 3 | 6.88 | 4.6 | 8.44
Paper (%) | 8 | 15.8 | 9.9 | 18.48

## Slide 10
Primary energy
In 2020, Vietnam's TPES was estimated at 95,762 KTOE, increased by only 1.5% compared with the previous year.
1
Primary energy use
The export output in 2019 was only 8,834 KTOE, a 2.4-fold decrease compared to 2010.
In 2019, energy imports reached 44,342 KTOE, a 39.6% increase compared to 2018.
2
Vietnam Energy Statistics 2020
CURRENT STATUS OF ENERGY USE IN VIETNAM

## Slide 11
Energy Intensity by Country
Considering population size, Vietnam's TPES per capita in 2018 was relatively low at only 848 kgOE/person, even lower than the ASEAN average of 1,041 kgOE/person. However, the TPES intensity per GDP was quite high. This indicates that Vietnam's energy efficiency needs improvement.
3
Amount of energy needed to produce one unit of economic output. A lower number means that economies produce economic value in a less energy-intensive way.
4
Energy intensity, 2000 to 2020
Vietnam Energy Statistics 2020
CURRENT STATUS OF ENERGY USE IN VIETNAM

## Slide 12: AVERAGE ELECTRICITY PRICE (2010 – 2024)
Chart: Graph of electricity price form 2009 to 2024
| Năm 2009 | Năm 2010 | Năm 2011 | Năm 2012 | Năm 2013 | Năm 2014 | Năm 2015 | Năm 2016 | Năm 2017 | Năm 2018 | Năm 2019 | Năm 2020 | Năm 2021 | Năm 2022 | Năm 2023 | Năm 2024
 | 948 | 1058 | 1242 | 1369 | 1508 | 1622 | 1622 | 1622 | 1622 | 1720 | 1864 | 1864 | 1864 | 1864 | 1920 | 2103
Electricity price comparison table of Vietnam with some countries in the world (Source: EVN 2022)
Electricity price of countries in the world
Converted to Vietnamese dong

## Slide 13: CURRENT STATUS OF ENERGY USE IN INDUSTRY
Proportion of energy consumption: The industrial sector accounts for about 54% of the total energy consumption in the country.
Industries with high energy consumption:
  The steel production, cement, textile, wood processing, and chemical industries. These industries consume approximately 70% of the total energy in the industrial sector.
  Seafood industry has 80-90 DEUs, represent 3.14% of the total number of industrial DEUs.
Energy efficiency in the seafood industry remains low, with significant waste due to outdated technology and inefficient management.

## Slide 14: ENERGY CONSUMPTION STRUCTURE IN THE INDUSTRY
Proportion of energy consumption by sector:
  Manufacturing sector: 60%
  Construction sector: 15%
  Mining sector: 10%
  Transportation and logistics sector 5%
Main types of energy used:
  Electricity: Account for the largest proportion in the energy consumption structure of the industrial sector.
  Oil and natural gas: Used in manufacturing and chemical industries.
  Coal: Mainly used in the cement and metallurgy industries.

## Slide 15: CAUSES OF HIGH ENERGY CONSUMPTION
Outdated technology: Many seafood processing enterprises still rely on outdated technologies that consume excessive energy and cause significant environmental pollution. These include inefficient refrigeration and freezing systems, manual processing lines, old boilers, and poor water and waste management practices. Such technologies lead to high operational costs, low product quality, and non-compliance with environmental and food safety standards. Upgrading to modern, energy-efficient equipment and implementing wastewater treatment and automation systems is essential to improve sustainability and competitiveness in the global market.
Lack of investment in innovation: Insufficient capital and motivation to invest in energy-efficient equipment and technology.
Low awareness of energy efficiency: Some enterprises have not prioritized energy efficiency measures in their production processes.

## Slide 16: CHALLENGES IN ENERGY MANAGEMENT AND UTILIZATION
Technological challenges: Many seafood enterprises use outdated technology, resulting in low energy performance and environmental pollution.
Cost challenges: The initial investment costs for energy-efficient technologies are high, causing many enterprises to hesitate to make changes.
Lack of strong supporting policies: Although there are policies encouraging energy efficiency, seafood enterprises still not effective enough to drive widespread adoption of energy efficiency measures among enterprises.

## Slide 17: TRENDS IN SUSTAINABLE DEVELOPMENT IN INDUSTRY
Green industry: Seafood enterprises are gradually paying more attention to using renewable energy and developing sustainable production.
International trend: Multinational corporations have higher standards for energy and environmental requirements when collaborating, especially in industries such as textiles and electronics.
Digital transformation and energy optimization: Applying digital technology to monitor and optimize energy usage in production.
New trends all place a certain emphasis on reducing greenhouse gas emissions in production and have become collaboration criteria for many major international corporations. This issue is becoming increasingly important and challenging for the industrial development of Vietnam. The sustainability trends are also relevant to or practiced by the Seafood industry.

## Slide 18
Seafood industry

## Slide 19: ENERGY INTENSITY IN KEY INDUSTRIES IN VIETNAM
Paper
Cement
Steel
Industry

## Slide 20: BENCHMARKING IN THE SEAFOOD INDUSTRY
Benchmarking | Other Relevant Requirements
According to Article 6 of Circular 52/2018/TT-BCT, benchmarks for the seafood processing sector up to the end of 2025 are as follows: | 
- Industrial processing of catfish products: 1,050 kWh/ton of equivalent product - Industrial processing of shrimp products: 2,050 kWh/ton of equivalent product | Facilities exceeding the SEC benchmark must develop and implement an EE improvement plan to meet the benchmarks stated in Article 5 of Circular 52/2018/TT-BCT. DOITs must be reported to annually by January 15 regarding the status of benchmark implementation. Facilities with SEC higher than the benchmarks must also report their EE improvement plans, including proposed EEMs and implementation plans, in accordance with Clause 1, Article 6 of Circular 52/2018/TT-BCT.

## Slide 21: OVERVIEW OF VIETNAM'S SEAFOOD PROCESSING INDUSTRY
Energy consumption
The seafood industry’s energy intensity higher than the average level of other sectors, including cement, paper, and beverage.
According to some studies by the Ministry of Industry and Trade and GIZ, the rate of energy consumption divided into main categories is as follows:
  Refrigeration and freezing systems: account for 45–70% of total electricity consumption;
  Cooking, steaming, drying, boiling…: account for 10–30% (depending on product type);
  Lighting, water pumping, ventilation…: account for the remainder.

## Slide 22
2. Forms and sources of energy used
Activity | Commonly used energy types
Offshore fishing | Diesel
Aquaculture | Electricity (pump, aerator), fuel (generator)
Seafood processing | Electricity (compressor, freezer, conveyor), steam (from boiler), industrial gas
Storage, cold storage | Electricity (cooling system, lighting, fan)
OVERVIEW OF VIETNAM'S SEAFOOD PROCESSING INDUSTRY

## Slide 23
3. Energy efficiency and waste
Lack of energy monitoring and control systems: most processing facilities have not invested in BMS systems or detailed measurement devices.
High power consumption but low efficiency equipment: such as old refrigeration compressors, no inverter, no dehumidification/automatic defrosting.
Not optimizing operation: for example, running the entire condenser even at low load, lack of regular maintenance causes large power loss.
Refrigerant leakage: causes reduced heat exchange efficiency and increased electricity consumption.
OVERVIEW OF VIETNAM'S SEAFOOD PROCESSING INDUSTRY

## Slide 24
4. Level of application of energy efficiency solutions
Some large export enterprises have started to deploy:
Variable frequency converters for compressor motors, pumps, fans;
Cogeneration systems for heat and electricity from condensing hot water;
Insulation of pipes and cold storage walls;
Upgrading LED lighting systems.
However, most small and medium enterprises have not paid due attention, due to:
Lack of initial investment capital;
Lack of awareness and technical level;
Unable to see the long-term benefits.
OVERVIEW OF VIETNAM'S SEAFOOD PROCESSING INDUSTRY

## Slide 25
5. Energy efficiency potential
OVERVIEW OF VIETNAM'S SEAFOOD PROCESSING INDUSTRY
Some large export enterprises have started to deploy:
Variable frequency converters for compressor motors, pumps, fans;
Cogeneration systems for heat and electricity from condensing hot water;
Insulation of pipes and cold storage walls;
Upgrading LED lighting systems.
However, most small and medium enterprises have not paid due attention, due to:
Lack of initial investment capital;
Lack of awareness and technical level;
Unable to see the long-term benefits.

## Slide 26
5. Energy saving potential (continued)
Energy consumption category | Electricity consumption rate | Savings potential (%) | Typical solutions
Refrigeration system (freezing, cold storage, flake ice) | 45–70% | 15–30% | Install inverter for refrigeration compressor Optimize condenser, evaporator Insulation, automatic defrost Freezing according to load
Cooking, steaming, drying system (using steam or electric resistance) | 10–30% | 10–25% | Utilize reflux steam Insulate tanks and pipes Automate the cooking process
Water pump motor, fan, aerator | 5–10% | 15–25% | Use IE3/IE4 motor Install inverter according to load Control pressure/flow according to demand
Illumination | 3–5% | 30–50% | Replace LED bulbs Install motion sensors Arrange lighting appropriately
Air compression system (if any) | 3–8% | 10–20% | Increase compressor efficiency Water and leakage separation Actual load control
OVERVIEW OF VIETNAM'S SEAFOOD PROCESSING INDUSTRY

## Slide 27: EEMs in the seafood processing industry

## Slide 28: EEMs in the seafood processing industry
1. Heat Recovery from Cooling Systems for Hot Water Production
Process:
Install heat exchangers in the cooling system to recover waste heat from the refrigeration compressors.
This recovered heat is used to heat water for sanitation and processing activities.
Integrate the heat exchanger with the existing system, minimizing installation time and costs.
Manage heat recovery through an automated system to ensure efficient utilization of thermal energy.
Benefits:
Saves energy used for heating water, reducing fuel or electricity consumption.
Shortens the payback period for the investment to 1.4–2.2 years.

## Slide 29: EEMs in the seafood processing industry
2. Direct Use of Chilled Water Instead of Flake Ice
Process:
Replace the use of flake ice with a direct cooling system that supplies chilled water at 2–5°C.
The chilled water can be reused in cooling processes for raw materials or finished products.
Implement a recirculation system to minimize water and energy waste.
Optimize the flow of chilled water to each production stage to prevent excess cooling energy usage.
Benefits:
Saves electricity consumption ranging from 220,000 to 660,000 kWh/year, depending on the plant’s scale.
Reduces operational costs and CO₂ emissions.

## Slide 30: EEMs in the seafood processing industry
3. Optimizing Refrigeration Systems
Optimization Steps:
Regularly inspect and maintain refrigeration equipment, such as compressors, evaporators, and condensers.
Install temperature and pressure sensors to monitor cooling performance and promptly detect issues.
Adjust and maintain storage, freezing, and refrigeration temperatures to match specific product requirements.
Use high-efficiency evaporator fans and regulate fan flow according to actual thermal loads.
Benefits:
Enhances cooling efficiency and reduces energy consumption by 20–30%.
Lowers operational and maintenance costs.

## Slide 31: EEMs in the seafood processing industry
4. Using High-Efficiency LED Lighting
Implementation:
Replace fluorescent or halogen bulbs with high-efficiency LED lighting throughout the factory.
Install automatic light sensors to adjust brightness based on production activity and ambient light levels.
Benefits:
Reduces electricity costs for lighting.
Saves 15–20% energy and extends the lifespan of lighting equipment.

## Slide 32: EEMs in the seafood processing industry
5. Optimizing the Steam System
Implementation:
Regularly maintain the boiler system to remove deposits and improve heat exchange efficiency.
Install economizers to recover heat from exhaust gases to preheat boiler feedwater.
Use effective insulation materials for steam pipelines, valves, and storage tanks.
Recover condensate from the steam system for reuse, reducing the need for new water and heating energy.
Benefits:
Reduces fuel consumption by 15–20%.
Increases boiler efficiency by 3–10%, extending equipment lifespan.

## Slide 33: EEMs in the seafood processing industry
6. Optimizing the Compressed Air System
Implementation:
Inspect and repair air leaks to prevent wastage, as leaks can account for 20–30% of total energy consumption.
Install variable frequency drives (VFDs) to adjust compressor speed based on actual demand, reducing energy use during low loads.
Optimize system operating pressure to match equipment requirements without exceeding necessary levels.
Recover waste heat from air compressors for use in activities like water heating or space heating.
Benefits:
Saves 15–35% of electricity consumption.
Recovers 50–90% of waste heat, reducing additional energy costs.

## Slide 34: EEMs in the seafood processing industry
7. Use solar energy
Install solar power system on factory roof.
Use solar energy for applications such as lighting, hot water.
Effective:
Reduce electricity costs by 20-30%.
Reduce greenhouse gas emissions, improve corporate image far and wide.

## Slide 35: EEMs in the seafood processing industry
8. Implementing an Energy Management System According to ISO 50001
Implementation Steps:
Establish an energy management system (EnMS) to monitor and optimize energy usage across the facility.
Set specific energy-saving targets, measure performance, and implement continuous improvements.
Integrate energy-saving criteria into the Key Performance Indicators (KPIs) of each department.
Conduct employee training on energy-saving awareness and techniques.
Benefits:
Reduces energy consumption by 5–20%.
Enhances production efficiency while meeting international environmental standards.

## Slide 36: EEMs in the seafood industry in the world
1. Whitby Seafoods' Energy Efficiency Initiatives
Company: Whitby SeafoodsLocation: United Kingdom (https://www.whitby-seafoods.com/)
Industry: Seafood Processing
Background: Whitby Seafoods, a leading UK scampi producer, faced challenges in monitoring and managing energy consumption across its manufacturing operations. With rising energy costs and a commitment to sustainability, the company sought to gain detailed insights into its energy usage to identify inefficiencies and implement corrective measures.

## Slide 37: EEMs in the seafood industry in the world
Implemented Measures: Deployment of RS Industria Monitoring System.
Whitby Seafoods collaborated with RS Industria to install a continuous energy monitoring system across 49 energy-intensive assets, including equipment in the cold storage, ammonia plant room, and packing and coating lines. This system enabled real-time data collection on energy consumption.
Results
Enhanced Visibility: The monitoring system provided detailed insights into energy consumption at the site, line, and asset levels, enabling more informed decision-making.
Rapid Identification of Inefficiencies: The real-time data allowed for the swift detection of inefficiencies, such as equipment running unnecessarily during non-production periods, leading to prompt corrective actions.
Promotion of Energy-Saving Culture: The initiative fostered greater awareness among employees regarding energy usage, encouraging behaviors aligned with the company's sustainability goals.
Source: rs-industria.com

## Slide 38: Q&A
1. What type of refrigerant is being used in the cold storage and freezing system? Is it still suitable in terms of efficiency and environment?
2. Is there a method of recovering waste heat from the compressor for use in steps such as washing fish and boiling water?
3. Has regular maintenance been performed and the cold loss through the door, gaskets, and panel shells checked?
4. Which of the measures we identified herein may be applicable to your facilities?

## Slide 39
THANK YOU