## Slide 1: TRAINING PROGRAMME FOR INDUSTRIAL ENTERPRISEs
Module 9.7:
Case studies in seafood industry in Vietnam
MANAGEMENT OFFICERS

## Slide 2: CONTENT
General information Case studies

## Slide 3
1
General information

## Slide 4: Overview of the Seafood Processing Industry
Vietnam’s seafood processing industry is a major export sector — >99% of production is exported for some companies.
Energy costs account for ~30% of total production cost in seafood processing & food manufacturing.
High energy consumption areas:
Cold storage & freezing
Processing lines
Lighting
Hot water production
Energy efficiency potential: 10–30% cost savings through technology upgrades, management practices, and renewable integration.

## Slide 5
2
Case studies

## Slide 6: 1. MINH PHÚ SEAFOOD CORPORATION
Vietnam’s No.1 seafood exporter (export turnover > 730 million USD in 2014; ranked 23rd among the world’s top 100 seafood companies) has achieved billions of VND in annual savings in electricity and DO fuel costs through bold energy efficiency investments.

## Slide 7: 1. Current Status
Current Status
Large shrimp processing & export facilities, operating multiple shifts daily.
High energy consumption from lighting, freezing systems, and boilers.
Previous technologies:
2,500 fluorescent light fixtures in processing plants.
Traditional IQF freezers with ~14 min freezing time for shrimp PTO 16/20.
DO-fueled steam boilers for hot water and processing.

## Slide 8: 2. Implemented Measures
1. LED Lighting Upgrade
Investment: Replaced 2,500 fluorescent fixtures with LED units.
Cost: LED 2.8B VND vs Fluorescent 1.2B VND.
Technical Specs: LED consumption = 18W; Fluorescent = 48W.
Energy Saving:
Annual LED electricity use: 583,200 kWh → 847M VND/year.
Annual fluorescent electricity use: 1,555,200 kWh → 2.33B VND/year.
Annual saving: 1.458B VND (≈121M/month).
Payback: ~13 months.
Extra Benefits: No breakage risk in food areas, 10× longer lifespan, no heat radiation → reduced air-conditioning load.
Using LED lights helps save electricity effectively at Minh Phu's factories.

## Slide 9: 2. Implemented Measures
2. High-Speed IQF Freezers
Previous system: Avg. freezing time = 14 min, high heat loss, large floor footprint.
New system: High-speed IQF + LVS + pneumatic defrost.
Results:
Freezing time reduced to 4.5–5 min.
Energy use reduced 21–28%.
Product loss <1%.
Stable freezing → improved product quality.
Extended operation up to 20 hrs before defrost needed.

## Slide 10: 2. Implemented Measures
3. Biomass Steam Boilers
Previous: DO-fueled boilers cost 460,848 VND/ton of product.
New: Biomass boilers cost 282,165 VND/ton.
Saving: 178,683 VND/ton (~45% reduction).
Environmental benefits:
Uses agricultural residues (rice husk, bagasse, sawdust, corn stalks).
Minimal SOx/NOx emissions compared to fossil fuels.
Diverts agricultural waste from landfill.

## Slide 11: 2. Implemented Measures
Measure | CAPEX (VND) | Annual Energy Cost Before | Annual Energy Cost After | Annual Saving | Payback Period
LED lighting | 2.8B | 2.33B | 0.847B | 1.458B | 13 months
High-speed IQF freezers | — | — | 21–28% reduction | — | —
Biomass boilers | — | 460,848 VND/ton | 282,165 VND/ton | 178,683 VND/ton | —
Results Summary Table

## Slide 12: 2. Implemented Measures
Key Takeaways
Integrated EE approach: lighting + freezing + renewable steam.
Savings scale: Billions VND/year in operating costs.
Sustainability: Lower CO₂ emissions, waste reuse, improved product quality.
Leadership in sector: Demonstrates competitive advantage through green production.

## Slide 13
Case Study 2 – Southern Fisheries Industry Co., Ltd.

## Slide 14: Current Status
Current Status: Large-scale seafood processing with monthly electricity costs averaging nearly 2 billion VND.

## Slide 15: Implemented Measures
Upgraded production lines with modern machinery and VSDs (Variable-Speed Drives).
Implemented ISO-quality management systems.
Installed a solar hot-water heating system to supply hot water for cleaning and sanitation of product containers.

## Slide 16
Results
Reduced monthly electricity consumption by approximately 15% (~300M VND/month).
Improved production efficiency, met environmental compliance standards, and enhanced export competitiveness.

## Slide 17
Case Study 3: CASEAMEX (Can Tho Import-Export Seafood JSC)

## Slide 18: 1. Current Status
Current Status
Processed seafood exporter managing energy-intensive operations across lighting, production lines, and refrigeration.
Prior to upgrades, electricity costs from factory facilities and machinery were substantial.

## Slide 19: Implemented Measures
Installed new-generation LED lighting across office buildings, factories, workshops, outdoor areas, and parking lots.
Installed energy monitoring meters on production lines.
Added variable-speed drives (VSDs) for high-power machinery.
Upgraded production with modern conveyors to enhance output while reducing energy use.
Installed up to 1 MWp rooftop solar PV system
Applied ESCO model for solar hot water systems
Launched internal campaigns encouraging staff to conserve energy “at all times, everywhere.”

## Slide 20: Results
Achieved nearly 30% reduction in monthly electricity costs.
Enhanced use of renewable energy and improved competitive edge in seafood exports

## Slide 21: Compare case studies
Summary Table: Case Studies in the Seafood Processing Industry
Company | Implemented Measures | Results
Minh Phú Seafood Corporation | Replaced 2,500 fluorescent lights with LEDs Upgraded to high-speed IQF freezers + LVS & pneumatic defrost Installed biomass-fired steam boilers | Annual electricity savings: 1.458 B VND (~121 M/month) Freezing time cut from 14 to ~5 minutes Energy use in freezing lowered by 21–28% Product loss <1%; enhanced quality Biomass fuel cut steam cost per ton by ~45%
Caseamex (Can Tho Seafood JSC) | Installed new-gen LED lighting across facilities Deployed energy meters and VSDs on machinery Upgraded conveyors and added 1 MWp rooftop solar Applied ESCO model for solar hot water systems Promoted energy-saving behaviors among staff | Monthly electricity cost reduced by ~30% Solar hot water cut 23,000 kWh (~40 M VND) in the first month; 36–40 M VND/month savings thereafter Easier system monitoring via ESCO service
Southern Fisheries Industry Co., Ltd. | Upgraded machinery and implemented VSDs Adopted ISO-quality management systems Equipped facility with solar water heating for sanitation | Monthly electricity consumption fell by ~15% (~300 M VND/month) Improved production efficiency, environmental compliance, and export competitiveness

## Slide 22: DISCUSSION
Trainees discuss about:
Please sharing the case study of energy saving in your company
Discuss and recommend in the case study above

## Slide 23
THANK YOU