## Slide 1
MEASUREMENT AND VERIFICATION (M&V)

## Slide 2
M&V
THE NATURE & BENEFITS OF M&V
M&V PLANNING
SIMULATION CALCULATION PRACTICE
Common Issues in M&V

## Slide 3
INTRODUCTION M&V

## Slide 4
What is M&V?
Measurement & Verification
The process of using measurement data to reliably determine the amount of energy saved in a building after implementing energy-saving measures.
Measurement
Data collection
Verification
Determining the amount of energy saved
Measurement

## Slide 5
DIFFERENTIATING M&V AND MONITORING
Criteria | M&V (Measurement & Verification) | Monitoring (System Monitoring)
Primary Purpose | Calculate & verify energy savings after implementing ECM | Monitoring and controlling system operations
Legal & Financial | Used in EPC contracts, carbon credits, ISO 50001 certification, etc. | Not directly used for verifying savings or payments
Usage data | May come from actual measurements, operational records, or monitoring systems | Real-time data from sensors, meters, BMS/EMS
Adjustment factors | Adjusted for operating conditions (output, weather, etc.) | No adjustment, raw data
Savings calculation | Yes (Baseline – Use ± Adjustments) | No (only monitors real-time consumption values)
Timing of implementation | Before and after ECM, periodically | Frequently, continuously
Applicable standards | IPMVP, ISO 50015, ASHRAE Guideline 14… | Not required by M&amp;V standards

## Slide 6
WHY IS M&V NECESSARY?
1. Increase energy efficiency
Understand the reality of savings, adjust operations accordingly
Maintain & enhance long-term savings
Good M&V programs =&gt; higher, more sustainable savings
2. Financial support & investment risk reduction
M&A builds trust for banks, investment funds, and lenders
Enables the development of off-balance-sheet financial models
Provides a guarantee basis for debt repayment cash flow
3. Promotes better design techniques
M&V design requires a thorough understanding of the system =&gt; contributes to improving design quality
Integration between technical efficiency and operational reality
4. Verifying and selling carbon credits (emission reductions)
M&V helps demonstrate CO2 reduction
As a basis for obtaining carbon credits (CDM, VCS, ETS, Mechanisms 6.2 – 6.4
5. Enhancing Transparency & Public Disclosure
Enhances credibility and public support for the project
Useful for sustainability reporting, meeting environmental standards: LEED, GRI, ISO 50001
6. Support national strategies & policies
Tool for implementing international commitments on climate change
Adopted by many countries to effectively manage energy use in projects

## Slide 7
THE ROLE OF M&V WITH STAKEHOLDERS
1. Investor/Project Owner
2. ESCO/Service Provider
Verifying whether a project is truly cost-effective or based on intuition
Settlement basis with EPC or ESCO contractors
Optimizing system operation and maintenance
Financial risk management
Demonstrating the technical effectiveness of energy conservation measures (ECM)
Revenue calculation based on performance contracts
Enhance credibility and create transparency with customers and investors

## Slide 8
THE ROLE OF M&V WITH RELATED PARTIES
3. Financial institution/Investor
Assessing financing capacity from cash flow savings
Implementing off-balance sheet financing models
Limiting project financing risks

## Slide 9
SOME CONCEPTS
Baseline period
A specific period of time used as a reference for comparison with the reporting period
Energy baseline
Quantitative standards established as a basis for comparing energy efficiency
Energy Performance Improvement Action (EPIA)
Actions/measures implemented/planned to achieve energy efficiency improvements
Energy consumption
The amount of energy used
Energy Performance Index (EnPI)
Quantitative value or measure of energy efficiency, as determined by the organization
Energy efficiency
Measurable results related to energy performance, energy use, and energy consumption

## Slide 10
METHOD FOR ESTABLISHING A BASELINE
Historical data
System modeling
Energy simulation
Use electricity/fuel bills or actual measurement data prior to the project
Applicable when operating conditions change significantly
Used for new projects or projects without historical data
Data must represent normal operating conditions
Use multivariate linear regression analysis to relate energy to variables: temperature, production, etc.
Use software: eQuest, EnergyPlus to simulate the baseline assumption
Regression statistics
Use energy data & independent variables (e.g., weather, production) to build a regression model

## Slide 11
OPERATING CONDITIONS
Concept:
Factors that directly affect energy consumption in buildings/equipment, apart from the impact of energy conservation measures (ECMs)
If these conditions change between the "before" and "after" implementation of ECMs
            Adjust the Baseline or Measured Use to determine the actual savings.
Download usage
Weather/Environment
Production/Production Activities
Maintenance level
Operating Procedures

## Slide 12
ENERGY SAVINGS
Energy Savings – The amount of energy no longer needed after implementing energy conservation measures (ECM) compared to previous consumption under equivalent conditions
Energy Savings = Ebaseline − Ereporting ± adjustments
Ebaseline: Energy used during the pre-improvement phase
Ereporting: energy measured after improvement
Δ adjustments: adjustments due to changes in operating conditions

## Slide 13
ENERGY SAVINGS
Detailed example:
The factory replaces high-efficiency motors:
Factors | Value
Electricity consumption before improvement (Baseline) | 120,000 kWh/year
Post-improvement consumption | 95,000 kWh/year
10% increase in production → adjustment + 10,000 kWh | (+) 10,000 kWh
 Actual savings = 120,000 – 95,000 + 10,000 = 35,000 kWh/year

## Slide 14
MEASUREMENT ERROR & UNCERTAINTY
MEASUREMENT ERROR
The deviation between the measured value and the actual value
Depends on the measuring device, installation method, and measurement environment
UNCERTAINTY
A measure of the reliability of energy-saving results
Includes random and systematic errors, affecting the accuracy of M&V reports

## Slide 15
MEASUREMENT ERROR & UNCERTAINTY
Accuracy of measuring devices
Electricity meter
Importance in finance
If the error is large  the sponsor does not trust  the project is difficult to borrow capital
High uncertainty  unacceptable risk in programs
Current Transformer (CT)
Temperature sensor
Air/water flow sensor

## Slide 16
PLANNING M&V

## Slide 17
M&V PLAN
Purpose: A foundation for determining accurate and verifiable savings.
Ensure all necessary data is available & budget control.
1
2
3
4
5
6
ECM Description
Define the measurement boundaries for savings
Documentation of the base year
Define post-retrofit phase &amp; adjustment
Describe design intent & commissioning process
Specify measurement options
Defining measurement points, measurement times, and measurement device characteristics
8
Describe the data analysis process and algorithms
7

## Slide 18
M&V PLAN
Purpose: A foundation for determining accurate and verifiable savings.
Ensure all necessary data is available & budget control.
9
10
11
12
13
14
For Option A: specify the assumed value &amp; impact
Option D: name of simulation software, input/output data
Quality Assurance (QA) process
Expected accuracy & qualitative impact
Method of reporting results, sample illustration
Third-party verification possible
Budget estimate, required resources
16
If future changes can be predicted, determine baseline
15

## Slide 19
ENERGY CONSUMPTION MEASUREMENT TECHNOLOGY
Energy consumption can be determined by
  Electricity or fuel bills, data from the main meter
  Separate measurement devices for retrofitted areas/equipment, capable of measuring in short cycles or continuously
  Separate measurement of parameters: power, operating time =&gt; total energy consumption
  Calibrated computer simulation
  Agreed-upon assumptions (stipulations) for high-reliability ECM parameters
The use of assumptions instead of actual measurements must be based on:
  The scope of identified savings
  Responsibilities among parties
  The potential impact of assumed errors

## Slide 20
INTRODUCTION TO 4 M&V OPTIONS (OPTION A-B-C-D)
Criteria | Option A Partial measurement – Improved isolation | Option B Full measurement – Improved isolation | Option C Entire system | Option D Simulation
 | Partially Measured Retrofit Isolation | Retrofit Isolation | Whole Facility | Calibrated Simulation
Measurement Range | Partial parameters Remaining Assumptions | Measure all parameters related to ECM | Measure total NL for the entire project | Simulation using software
Accuracy | Average Depends on assumptions | High | Dependent on the quality of the regression model | High if the model is correct
Cost | Low | Moderate to high | Low (invoice processing) | High (software, accurate data)

## Slide 21
INTRODUCTION TO 4 M&V OPTIONS (OPTION A-B-C-D)
Criteria | Option A Partial measurement – Improved isolation | Option B Full measurement – Improved isolation | Option C Entire system | Option D Simulation
Typical application | Lighting, small pumps | HVAC, motors, fans, chillers | Buildings, factories, shopping malls | Projects without historical data
Data requirements | Continuous short-term measurement combined with assumed values | Continuous short-term measurement | Analysis of main or secondary meter data | Energy usage simulation, calibrated using billing data
Adjustment analysis | Manual or simple | May require a small model | Requires statistical regression | Based on model assumptions

## Slide 23
PRACTICAL CALCULATIONS

## Slide 24
OPTION A – PARTIAL MEASUREMENT – IMPROVED ISOLATION
Illustrative example
Replace a 40W fluorescent bulb with a 20W LED bulb
Assumption: 10 hours of use per day. 300 days per year
Measurement: Electricity consumption rate of 1 light bulb
Calculation method:
Savings = (40W – 20W) x 10h x 300 days = 60,000 Wh = 60 kWh/year/bulb
Advantages | Limitations
Cost-effective, easy to implement Suitable for large numbers of identical devices | Average accuracy Not suitable if the operating load varies significantly or there are many influencing factors.

## Slide 25
OPTION B – FULL MEASUREMENT - IMPROVED ISOLATION
Illustrative example
The company replaced the old water pump with a high-efficiency motor integrated with a variable speed drive (VSD)
Actual measurement data
Before retrofit:
      Average measured power: 10.5 kW
      Operating time: 16 hours/day
      Recorded over 7 consecutive days
    After retrofitting
      Average measured power: 6.8 kW
      Constant operating time: 16 hours/day
      Recorded over 7 consecutive days
Calculation method:
Savings (kWh) = (10.5 kW – 6.8 kW) x 16 x 30 x 365 = 21,608 kWh/year

## Slide 26
OPTION C – ENTIRE FACILITY
Illustrative example
A 6-story office building implements multiple energy conservation measures (ECMs)
Replacing all lighting in the building with LEDs
Optimizing the HVAC system with BMS
Installing variable frequency drives for water pumps & AHU fans
Energy savings assessment based on the building's total electricity bill
Electricity bill data
Month | Pre-improvement consumption (2023) | Post-improvement consumption (2024) | Average temperature
January | 120,000 kWh | 105,000 kWh | 20.0 °C
February | 115,000 kWh | 97,000 kWh | 22.0°C
March | 125,000 kWh | 109,000 kWh | 26.5°C

## Slide 27
OPTION C – ENTIRE FACILITY
 Monthly electricity savings
Month | Electricity savings (kWh)
Month 1 | 120,000 – 105,000 = 15,000
February | 115,000 – 97,000 = 18,000
March | 125,000 – 109,000 = 16,000
Total savings for 3 months = 15,000 + 18,000 + 16,000 = 49,000 kWh
 Estimated financial savings
Assuming average electricity price: 2,000 VND/kWh
3-month savings = 49,000 x 2,000 = 98,000 VND

## Slide 28
OPTION D – STANDARD EFFECT SIMULATION
Illustrative example
A new data center built in 2024, featuring energy conservation measures (ECMs)
Installation of a high-efficiency cooling system (inverter chiller)
Well-insulated enclosure design (walls, roof)
LED lighting system and sensor calibration
New construction, no baseline data available

## Slide 29
OPTION D – SIMULATION OF STANDARD EFFECT
 Compare simulation results &amp; actual results
Deviation = 765,000 – 720,000 = 45,000 kWh
Relative error = (acceptable)
Data | Value
Floor area | 5,000 m²
Design simulation model | Prediction: 720,000 kWh/year
Actual meter reading data | Recorded: 765,000 kWh/year
Simulation climate data | TMY weather file for Hanoi
Actual weather in 2024 | Slightly different from TMY (with 5 unusually hot days)
 Estimated savings
Building model without ECM: 880,000 kWh/year
Model with ECM (calibrated): 720,000 kWh/year
Savings = 160,000 kWh/year
 Use energy simulation software (EnergyPlus, eQuest, IESVE, DOE-2)

## Slide 30
COMMON ISSUES

## Slide 31
COMMON ISSUES
Factors affecting energy efficiency
Many factors affect equipment performance &amp; savings levels
Predictable and measurable factors can be used for routine adjustments
Assessing the uncertainty of savings
Arising from: measurement device errors, model errors, sampling errors, regulatory assumptions
Quantifiable factors should be quantified, and non-quantifiable factors should be qualitatively assessed
Minimum energy performance standards
If there are regulations or internal standards, the baseline can be set using this minimum standard
Unmeasurable, unpredictable factors cause fluctuations and must be addressed through extraordinary adjustments
Uncertainty can be reduced by using measured data and increasing sample size

## Slide 32
COMMON ISSUES
Minimum operating conditions
The ECM shall not be degraded in operating conditions without the user's consent
Energy pricing
Prices are applied from the energy price list or marginal price, taking into account all factors on the bill
Third-party verification
An independent third party may assist the investor in verifying the M&V plan and savings report
The operating conditions to be maintained must be clearly stated in the M&V Plan
May be experienced but not yet licensed

## Slide 33
COMMON ISSUES
Data for the emissions trading program
Basis for verifying savings in the emissions trading program
Adjustment of the non-routine baseline
Applicable when unexpected changes occur: increase in area, equipment changes, operational targets
Weather data & costs
Prioritize government-published data, on-site data
Need to separate electricity savings by season, peak/off-peak hours, and fuel type if different EFs apply
Requires a method to track changes
Costs depend on ECM complexity, number of measurement points, independent variables, and measurement time